## Sheet1
Project Number: 123 |  | Project Name: EXAMPLE BUILDING
Graphic Logic Location |  | Point Name Mnemonic |  | Point | Hardware Point |  |  |  | Virtual | Notes See Page # Note
| Point Description | System | Point | Type | DO | DI | AO | AI | Point | Comments | #
1 | Room Temperature | VAV# | BxyzRT | RTS1 |  |  |  | 1
2 | Room Temperature Setpoint | VAV# | BxyzRT_SP | V |  |  |  |  | 1
3 | Room Trendlog | VAV# | BxyzRT_TL | TL |  |  |  |  | 1 | RT,RT_SP,F,F_SP
| Room Override | VAV# | BxyzOR | CRS |  | 1
4 | Room Override Time Left | VAV# | BxyzOR_T | V |  |  |  |  | 1 | Set 60 min
5 | Room Weekly Schedule | VAV# | BxyzWS | WS | [5 empty] | See Spec 15925
6 | Flow | VAV# | BxyzF | FS |  |  |  | 1
7 | Flow Setpoint | VAV# | BxyzF_SP | V |  |  |  |  | 1
8 | Damper | VAV# | BxyzD | DA1 |  |  | 1
| Temperature Controller | VAV# | BxyzRT_CO | CO |  |  |  |  | 1 | use RT:RT_SP
| Flow Controller | VAV# | BxyzF_CO | CO |  |  |  |  | 1 | use F:F_SP
9 | Program | VAV# | BxyzPG | PG |  |  |  |  | 1
10 | Minimum Flow Setpoint | VAV# | BxyzFMIN_SP | V |  |  |  |  | 1
11 | Maximum Flow Setpoint | VAV# | BxyzFMAX_SP | V |  |  |  |  | 1
| Total |  |  |  | 0 | 1 | 1 | 2 | 9
NOTE: x = Floor #
yz = Box # of Floor #
For VAV# and Box # see mechanical schedule
EXAMPLE