15900		Controls General

All controls are referred to as the Client Comfort System (CCS).  All controls shall be computerized direct digital except where noted in the following specification.

15910		Scope of Work

Provide a Client Comfort System, as specified in this document, for the Example Building.  CCS shall be accessed remotely via modem.  The operating system of the CCS shall operate in Windows 3.1 or higher, and shall coexist with other vendor’s systems, presently operating in Windows, to provide a multi-vendor work station at the BCBC Property Management Unit Office.

15920		Job Specific Alterations to BCBC Performance Specifications

EXAMPLE

No communication computers will be provided for this project.  Communication will be via modem with existing computer at the Property Management Unit.  Contractor shall make the CCS operating system operational on this computer and demonstrate remote communication to system.  Computer will meet Corporation hardware and set up standards and will have at least 10 MB of disk space.

15925		Smoke/Fire Sequence

The following smoke sequences shall be incorporated in the Client Comfort System.

When fire alarm system is activated both VAV1 and VAV2 shall shut down via a hardware connection to the fire panel.  If the fire department activates a particular fan system for smoke removal, a smoke override switch on the fire panel shall restore power to the fan control circuits and a smoke override VAV1 SMOKE1_OVR or smoke override VAV2 SMOKE2_OVR relay shall be turned on .  These are two separate digital inputs to the CCS connected to the smoke relays on the fire panel.  These points are shown as part of the CCS on the Miscellaneous Point Sheet.

The following smoke sequence shall be added to the Generic Start Up Code for VAV1 (BCBC Variable Volume Type L) and VAV2 (BCBC Variable Volume Type A).

VAV1 modify 2.2 to read:

EXAMPLE

IF WS ON OR RT_AVG < 14 OR SMOKE1_OVR THEN

START RF

IF SMOKE1_OVR OFF AND WS OFF AND RT_AVG > 16 THEN

STOP RF

VAV2 modify 1.3 to read:

IF WS ON OR RT_AVG < 14 OR SMOKE2_OVR THEN

START SF

IF SMOKE2_OVR OFF AND WS OFF AND RT_AVG > 16 THEN

STOP SF

Add as last line of 3.2 VAV1 and VAV2:

IF SAT > 5 AND SMOKEx_OVR THEN

MAD = 100

ELSE

MAD = MAD_CO

The following smoke sequence shall be added to the Generic Start Up Code for BCBC Variable Air Volume TUC (Type V-A) and (Type V-N).

Add as last line of 9 Box Program:

IF SMOKEx_OVR THEN BxyzF_SP = BxyzFMAX

(Apply to all boxes.)