## Sheet1
Project Number: |  | Project Name:
Graphic Logic Location |  | Point Name Mnemonic |  | Point | Hardware Point |  |  |  | Virtual | Notes See Page # Note
| Point Description | System | Point | Type | DO | DI | AO | AI | Point | Comments | #
1 | Chiller Control |  | ENBL | CR1 | 1
2 | Chiller Status |  | S | CRS |  | 1
3 | Chiller Program |  | PG | PG |  |  |  |  | 1
4 | Chiller Run Hours |  | TZ | TZ |  |  |  |  | 1
5 | Chiller Vane |  | VANE | DDC |  |  | 1
| Chiller Vane Controller |  | VANE_CO | CO |  |  |  |  | 1 | use RWT:RWT_SP
| Chiller Vane Low Limit Controller |  | VANE_CO_LL | CO | [5 empty] | use SWT:SWT_LL_SP
| Chiller Vane Ramp |  | RAMP | V |  |  |  |  | 1
6 | Chiller Trendlog |  | TL | TL |  |  |  |  | 1 | VANE,SWT,RWT,ENBL
7 | Chilled Water Pump |  | P1 | CR1 | 1
8 | Chilled Water Pump Status |  | P1_S | V |  |  |  |  | 1
9 | Chilled Water Pump Amps |  | P1_AMP | CS1 |  |  |  | 1
10 | Chilled Water Pump Run Hours |  | P1_TZ | TZ |  |  |  |  | 1
11 | Condenser Pump Status |  | P2_S | V |  |  |  |  | 1
12 | Condenser Pump Amps |  | P2_AMP | CS1 |  |  |  | 1
13 | Condenser Pump Run Hours |  | P2_TZ | TZ |  |  |  |  | 1
14 | Supply Water Temperature |  | SWT | PTS1 |  |  |  | 1
| Supply Water Low Limit Setpoint |  | SWT_LL_SP | V |  |  |  |  | 1
15 | Return Water Temperature |  | RWT | PTS1 |  |  |  | 1
16 | Return Water Setpoint |  | RWT_SP | V |  |  |  |  | 1
17 | Cooling Tower RW Temp |  | CT_RWT | PTS1 |  |  |  | 1
18 | Cooling Tower RW Setpoint |  | CT_RWT_SP | V |  |  |  |  | 1
19 | Cooling Tower SW Temp |  | CT_SWT | PTS1 |  |  |  | 1
20 | Cooling Tower Fan Control |  | CT | CR1 | 1
21 | Cooling Tower Fan Status |  | CT_S | CRS |  | 1
22 | Cooling Tower Program |  | CT_PG | PG |  |  |  |  | 1
23 | Cooling Tower Trendlog |  | CT_TL | TL |  |  |  |  | 1 | RWT,SWT,CT,OAT
| Total |  |  |  | 3 | 2 | 1 | 6 | 14