## Sheet1
Project Number: |  | Project Name:
Graphic Logic Location |  | Point Name Mnemonic |  | Point | Hardware Point |  |  |  | Virtual | Notes See Page # Note
| Point Description | System | Point | Type | DO | DI | AO | AI | Point | Comments | #
1.1 | Supply Fan Outdoor Air Damper |  | SF_OAD | CR1 | 1 |  |  |  |  | Wire end switch to SF
| Damper Actuator |  |  | DA4/A
1.2 | Supply Fan Amps |  | SF_AMP | CS1 |  |  |  | 1
| Supply Fan Status |  | SF_S | V |  |  |  |  | 1
1.3 | Supply Fan Program |  | SF_PG | PG |  |  |  |  | 1
1.4 | Supply Fan Trendlog |  | SF_TL | TL |  |  |  |  | 1 | SF_S,SF_AMP,SAP,SAP_SP
1.5 | Supply Fan Run Hours |  | SF_TZ | TZ |  |  |  |  | 1
1.6 | Weekly Schedule |  | WS | WS |  |  |  |  | 1
2.1 | Heating Coil Valve |  | HCV | CV3 |  |  | 1
| Heating Coil Controller |  | HCV_CO | CO |  |  |  |  | 1 | use SAT:SAT_SP
2.2 | Heating Program |  | HTG_PG | PG |  |  |  |  | 1
2.3 | Heating Trendlog |  | HTG_TL | TL |  |  |  |  | 1 | HCV,SAT_SP,SAT,HCP
2.4 | Heating Coil Pump |  | HCP | CR1 | 1
2.5 | Heating Coil Pump Run Hours |  | HCP_TZ | TZ |  |  |  |  | 1
3.1 | Freeze Control |  | FRZ | FRZ |  | 1
4.1 | Exhaust Fan Start/Stop |  | EF | CR1 | 1
4.2 | Exhaust Fan Amps |  | EF_AMP | CS1 |  |  |  | 1
| Exhaust Fan Status |  | EF_S | V |  |  |  |  | 1
4.3 | Exhaust Fan Program |  | EF_PG | PG |  |  |  |  | 1
4.4 | Exhaust Fan Trendlog |  | EF_TL | TL |  |  |  |  | 1 | EF,EF_AMP
4.5 | Exhaust Fan Run Hours |  | EF_TZ | TZ |  |  |  |  | 1
5.1 | Supply Air Temperature |  | SAT | DTS2 |  |  |  | 1
5.2 | Supply Air Temp Setpoint |  | SAT_SP | V |  |  |  |  | 1
5.3 | Supply Air Temp Program |  | SAT_PG | PG |  |  |  |  | 1
| Total |  |  |  | 3 | 1 | 1 | 3 | 15