## Sheet1
Project Number: |  | Project Name:
Graphic Logic Location |  | Point Name Mnemonic |  | Point | Hardware Point |  |  |  | Virtual | Notes See Page # Note
| Point Description | System | Point | Type | DO | DI | AO | AI | Point | Comments | #
1 | Heating Supply Water Temp |  | SWT | PTS1 |  |  |  | 1
2 | Heating Return Water Temp |  | RWT | PTS1 |  |  |  | 1
3 | Boiler Return Water Temp |  | B_RWT | PTS1 |  |  |  | 1
4 | Heating Supply Water Setpoint |  | SWT_SP | V |  |  |  |  | 1
5 | Heating Supply Water Program |  | SWT_PG | PG |  |  |  |  | 1
6 | Heating Supply Water Trendlog |  | SWT_TL | TL |  |  |  |  | 1 | SWT,SWT_SP,RWT,OAT
7 | Expansion Tank Pressure |  | XT_PSP | PS1 |  |  |  | 1
8.1 | System Pressure |  | SYS_PSP | PS1 |  |  |  | 1
8.2 | System Pressure Setpoint |  | SYS_PSP_SP | V |  |  |  |  | 1
8.3 | System Pressure Program |  | SYS_PSP_PG | PG |  |  |  |  | 1
9.1 | Heating Pump 1 Control |  | P1 | CR1 | 1
9.2 | Heating Pump 1 Run Hours |  | P1_TZ | TZ |  |  |  |  | 1 | use P1
9.3 | Heating Pump 1 ASD |  | P1_ASD | DDC |  |  | 1
| ASD Controller |  | P1_ASD_CO | CO |  |  |  |  | 1 | use SYS_PSP:SYS_PSP_SP
10.1 | Heating Pump 2 Control |  | P2 | CR1 | 1
10.2 | Heating Pump 2 Run Hours |  | P2_TZ | TZ |  |  |  |  | 1 | use P2
11 | Heating Pump Program |  | P_PG | PG |  |  |  |  | 1
12 | Heating Pump Trendlog |  | P_TL | TL |  |  |  |  | 1 | P1_ASD,SYS_PSP,SYS_PSP_SP
13 | Boiler Control Program |  | BLR_PG | PG |  |  |  |  | 1
14.1 | Boiler 1 Pump Control |  | BLR1_P | CR1 | 1
14.2 | Boiler 1 Pump Run Hours |  | BLR1_P_TZ | TZ |  |  |  |  | 1
14.3 | Boiler 1 Supply Water Temp |  | BLR1_SWT | PTS1 |  |  |  | 1
14.4 | Boiler 1 SWT Trendlog |  | BLR1_SWT_TL | TL |  |  |  |  | 1 | RWT,BLR1_P,BLR1_SWT
15.1 | Boiler 2 Pump Control |  | BLR2_P | CR1 | 1
15.2 | Boiler 2 Pump Run Hours |  | BLR2_P_TZ | TZ |  |  |  |  | 1
15.3 | Boiler 2 Supply Water Temp |  | BLR2_SWT | PTS1 |  |  |  | 1
15.4 | Boiler 2 SWT Trendlog |  | BLR2_SWT_TL | TL |  |  |  |  | 1 | RWT,BLR2_P,BLR2_SWT
__.1 | Boiler Pump Control |  | BLR _P | CR1 | [5 empty] | As Required
__.2 | Boiler Pump Run Hours |  | BLR _P_TZ | TZ | [5 empty] | As Required
__.3 | Boiler Supply Water Temp |  | BLR _SWT | PTS1 | [5 empty] | As Required
__.4 | Boiler SWT Trendlog |  | BLR _SWT_TL | TL | [5 empty] | As Required
| Total |  |  |  | 4 | 0 | 1 | 7 | 15