## Sheet1
Project Number: |  | Project Name:
Graphic Logic Location |  | Point Name Mnemonic |  | Point | Hardware Point |  |  |  | Virtual | Notes See Page # Note
| Point Description | System | Point | Type | DO | DI | AO | AI | Point | Comments | #
1 | Room Temperature |  | BxyzRT | RTS1 |  |  |  | 1
2 | Room Temperature Setpoint |  | BxyzRT_SP | V |  |  |  |  | 1
3 | Room Trendlog |  | BxyzRT_TL | TL |  |  |  |  | 1 | RT,RT_SP,F,SAT
| Room Override |  | BxyzOR | RTS1 |  | 1 |  |  |  | Button on sensor
4 | Room Override Time Left |  | BxyzOR_T | V |  |  |  |  | 1 | Set 60 min
5 | Room Weekly Schedule |  | BxyzWS | WS | [5 empty] | See Spec 15925
6 | Cold Duct Damper |  | BxyzCDD | DA1 |  |  | 1
7 | Box Program |  | Bxyz_PG | PG |  |  |  |  | 1
8 | Hot Duct Damper |  | BxyzHDD | DA1 |  |  | 1
9 | Cold Duct Flow |  | BxyzCDF | VS2 |  |  |  | 1
10 | Cold Duct Flow Setpoint |  | BxyzCDF_SP | V |  |  |  |  | 1
11 | Box Supply Air Temperature |  | BxyzSAT | DTS2 |  |  |  | 1
12 | Box Supply Air Temp Setpoint |  | BxyzSAT_SP | V |  |  |  |  | 1
13 | Box Supply Air Trendlog |  | BxyzSAT_TL | TL |  |  |  |  | 1 | HDSAT,CDSAT,SAT,SAT_SP
14 | Minimum Flow Setpoint |  | BxyzFMIN_SP | V |  |  |  |  | 1
15 | Maximum Flow Setpoint |  | BxyzFMAX_SP | V |  |  |  |  | 1
| Temperature Controller |  | BxyzRT_CO | CO |  |  |  |  | 1 | use RT:RT_SP
| Flow Controller |  | BxyzF_CO | CO |  |  |  |  | 1 | use F:F_SP
| Hot Duct Temp Controller |  | BxyzHDT_CO | CO |  |  |  |  | 1 | use SAT:SAT_SP
| Hot Duct Flow Controller |  | BxyzHDF_CO | CO |  |  |  |  | 1 | use F:FMAX_SP
16 | Hot Duct Flow |  | BxyzHDF | VS2 |  |  |  | 1
17 | Hot Duct Flow Setpoint |  | BxyzHDF_SP | V |  |  |  |  | 1
18 | Total Box Flow |  | BxyzF | V |  |  |  |  | 1
19 | Total Box Flow Setpoint |  | BxyzF_SP | V |  |  |  |  | 1
20 | Box Flow Trendlog |  | Bxyz_TL | V |  |  |  |  | 1 | HDF,CDF,F,F_SP
| Total |  |  |  | 0 | 1 | 2 | 4 | 17
NOTE: x = Floor #
yz = Box # of Floor #
For VAV# and Box # see mechanical schedule