## Sheet1
Project Number: |  | Project Name:
Graphic Logic Location |  | Point Name Mnemonic |  | Point | Hardware Point |  |  |  | Virtual | Notes See Page # Note
| Point Description | System | Point | Type | DO | DI | AO | AI | Point | Comments | #
1 | Room Temperature |  | BxyzRT | RTS1 |  |  |  | 1 |  | Wire OR button in parallel
2 | Room Temperature Setpoint |  | BxyzRT_SP | V |  |  |  |  | 1
3 | Room Trendlog |  | BxyzRT_TL | TL |  |  |  |  | 1 | RT,RT_SP,RCV,RCV_CO
4 | Room Override |  | BxyzOR | V |  |  |  |  | 1
5 | Room Weekly Schedule |  | BxyzWS | WS | [5 empty] | See Spec 15925
6 | Reheat Electric Mod Ctrl |  | BxyzRCE |  |  |  | 1 |  |  | 0-10 VDC interface
| Reheat Coil Controller |  | BxyzRCE_CO | CO |  |  |  |  | 1 | use SAT:SAT_SP
7 | Reheat Coil Program |  | BxyzRCE_PG | PG |  |  |  |  | 1
8 | Supply Air Temperature |  | BxyzSAT | DTS1 |  |  |  | 1
9 | Supply Air Temp Setpoint |  | BxyzSAT_SP | V |  |  |  |  | 1
| Room Temperature Controller |  | BxyzRT_CO | CO |  |  |  |  | 1 | use RT:RT_SP
| Total |  |  |  | 0 | 0 | 1 | 2 | 7
NOTE: x = Floor #
yz = Box # of Floor #
For VAV# and Box # see mechanical schedule