ÒCLIENT COMFORT SYSTEM (CCS)Ó

PERFORMANCE SPECIFICATIONS SECTION 15940

For Lease Projects

PS 1 - OPERATOR INTERFACE

1.1 Access Requirements

1.2 Access Security

1.3 Modem Requirements

1.4 Operator Interface Software

1.5 Static Screen Graphics Generation Software

1.6 Temporary Operator Interface

PS 2 - PROGRAMMABILITY

2.1 Database Creation and Modification

2.2 Alarm Definition and Processing

2.3 Trends

2.4 Trend Graphing

2.5 Totalization

2.6 Scheduling

2.7 Point Definitions

.1 Analog Points

.2 Digital Points

2.8 Software Controllers

2.9 Operator Control Language (OCL) Capabilities

2.10 OCL Editor

PS 3 - HARDWARE FEATURES

3.1 Panel Definitions

3.2 Power Conditioning

3.3 Power Failure Protection

3.4 Hardware Failure Isolation

3.5 Ease of Hardware Replacement

3.6 Database Back-Up and Off-Line Storage

3.7 Memory

3.8 SAP Processing Speed

3.9 System Display Speed

PS 4 - INTRA-SYSTEM COMMUNICATION

4.1 Network Communications

.1 Stand-Alone Panels (SAPs)

.2 Terminal Unit Controllers (TUCs)

4.2 System  Processing Speed

PS 5 - FIELD DEVICES

5.1 General

5.2 Point Type “CRS”

5.3 Point Type “CR1”

5.4 Point Type “CR2”

5.5 Point Type “CR3”

5.6 Point Type “CS1”

5.7 Point Type “CS2”

5.8 Point Type “CV1”

5.9 Point Type “CV2”

5.10 Point Type “CV3”

5.11 Point Type “CV4”

5.12 Point Type “DA1/x”

5.13 Point Type “DA2/x”

5.14 Point Type “DA3/x”

5.15 Point Type “DA4/x”

5.16 Point Type “DDC”

5.17 Point Type “DHS”

5.18 Point Type “DPS/x”

5.19 Point Type “DTS1/x”

5.20 Point Type “DTS2”

5.21 Point Type “EPT1”

5.22 Point Type “FRZ”

5.23 Point Type “GAS1”

5.24 Point Type “GAS2”

5.25 Point Type “GAS3”

5.26 Point Type “GAS4”

5.27 Point Type “GAS5”

5.28 Point Type “LS1”

5.29 Point Type “LS2”

5.30 Point Type “OS1”

5.31 Point Type “OTS”

5.32 Point  Type “PS1”

5.33 Point Type “PTS1”

5.34 Point Type “PTS2”

5.35 Point Type “RHS”

5.36 Point Type “RTS1”

5.37 Point Type “RTS2”

5.38 Point Type “RTS3”

5.39 Point Type “VS1”

5.40 Point Type “VS2”

5.41 Point Type “WPS”

PS 6 - OPERATING SYSTEM SOFTWARE POINT REQUIREMENTS

6.1 General

6.2 Point Type "AL"

6.3 Point Type "AS"

6.4 Point Type "CO"

6.5 Point Type "PG"

6.6 Point Type "TL"

6.7 Point Type "TZ"

6.8 Point Type "V"

6.9 Point Type "WS"

# PS 1 - OPERATOR INTERFACE

## 1.1	Access Requirements

.1	All functions of the system, storage of data, execution of commands, editing of programs, creation and display of graphics, etc., must be available regardless of the method of access to the system.  Functionality must not be dependent on a continuous connection to the CCS in the building, as there may not be a PC installed on-site.

.2	The Corporation will be accessing the CCS through Corporation Standard equipment by the following methods:

.1	Through an on-site desktop or notebook PC, connected to the CCS, but not necessarily permanently installed.

.2	Through either a desktop PC or a notebook PC, which will connect to the CCS periodically by modem.

.3	The Corporation requires two modes of access to the CCS:

.1	Through a text based terminal emulation interface available at all points of connection to the CCS.

.2	Through the full graphics interface described below, where the graphics are resident on any PC, whether connected directly to the CCS or remotely through the modem.

.4	Refer to Section 15920 for the access requirement for this project.

## 1.2	Access Security

.1	The system shall have a minimum of 4 levels of password access security.

## 1.3	Modem Requirements

.1	Provide and install, (complete with connecting cables), an auto-dial, auto-answer modem that shall allow access at any incoming lower speed, (minimum: US Robotics Sportser 33,600 baud).

.2	BCBC will provide for the installation of the phone line for the modem.

## 1.4	Operator Interface Software

.1	Provide in disk format 2 copies of all software required to access the control system and carry out all the specified operator interface functions.  This software will be for Corporation use only, from either on-site or remote access locations.  Include  for any licensing costs for the software.

.2	The operator interface software provided with the system shall be capable of operating on a workstation running Microsoft NT 4.0 operating system.

.3	Provide the following dynamic graphic data display capabilities:

.1	Dynamic data display on each graphic which can accommodate any combination of dynamic (point type) information, graphic symbols and text, displayed at any location on the entire screen.

.2	User control over attributes of dynamic data for display, including:

¥	values

¥	units

¥	point names and full descriptions

¥	auto/manual indication

¥	access to full point parameters

¥	text size

.3	Dynamic linking of screens via definition of Òhot spotsÓ at any location on screen.

.4	User definable sizing of Òhot spotsÓ and ability to control colour and transparency of same.

.5	User-controllable automatic update of dynamic data.

.6	Minimum of 64 dynamic graphic displays per stand-alone panel.

.7	Minimum of 100 points per graphic display.

.8	Ability to print directly from screen, to either a black & while, or colour printer.

.9	Automatic display of alarm indication and the ability to disable auto-display of graphic.

## 1.5	Static Screen Graphics Generation Software

.1	Provide static, colour graphics generation software to run on Corporation standard equipment.

.2	Software must provide the following capabilities:

.1	System that allows user to create, modify, and delete static graphics screens.

.2	Minimum VGA resolution with sixteen colour capability.

.3	Mechanism for copying and editing graphics of similar layout.

.4	Mechanism for importing Windows graphics file formats, such as TIFF, GIF, PCX, DXF, BMP.

.5	Graphics creation features shall provide:

¥	User creation of symbols that can be stored for future use.

¥	Control of symbol location on screen.

¥	Control of line drawing, type, colour and thickness.

¥	Control of infill colour, background colour.

¥	Control of alpha-numeric text, including font size and colour.

## 1.6	Temporary Operator Interface

The contractor shall provide a temporary, fully functional operator interface and alarm printer for the duration of the startup, commissioning, training and for the SEVEN(7)-day test.

# PS 2 - PROGRAMMABILITY

## 2.1	Database Creation and Modification

.1	Provide means for addition, deletion, definition and modification of points and point types through the operator interface.

.2	Provide links in the database such that if a point name is changed in database, all database occurrences of that point will automatically be changed.

.3	Provide direct keyboard override of all physical and virtual points with an indication on the display of any point that is operating under a keyboard override.

.4	The database for each physical or virtual point must only require definition once, regardless of the number of locations where it is used.

## 2.2	Alarm Definition and Processing

Provide the following:

.1	Operator defined digital and analogue alarms including operator defined limits and differentials from set points.

.2	Auto lockout of alarms when alarmed system is commanded off.

.3	Auto display of operator defined alarm messages.

.4	Operator defined routing of alarms.

.5	Log of points in alarm.

## 2.3	Trends

.1	Provide point trend logging capability for any system point as follows:

.1	User defined start/stop time or continuous trending.

.2	Sampling period user-adjustable from 5 seconds to 24 hours as a minimum.

.3	Change of value or change of state initiated.

.4	Display and print a minimum of 4 points simultaneously across the page.

.5	Ability to automatically dump trend logs to disk in ASCII format.

## 2.4	Trend Graphing

.1	System shall have the ability to graphically display logs or trended points in colour:

.1	Capability for display of a minimum of 4 points simultaneously, both analog and digital on the same graph.

.2	Capability for auto-scaling and ability to manually control horizontal and vertical scales.

## 2.5	Totalization

.1	Provide the capability to totalize the runtime of  all digital points.

.2	Each totalizer shall record the total runtime and total number of starts from a resettable start date.

## 2.6	Scheduling

.1	Provide scheduling feature that allows for creation of start/stop schedules and their use in programs as follows:

.1	Weekly	- day

-	4 stops/start times per day

-	direct override by Annual Schedules

-	direct override by system point

.2	Annual	-entire calendar year available

## 2.7	Point Definitions

### .1	Analog Points

.1	System shall have the capability to accommodate user defined scale ranges which can be attached to any input or output.

.2	Provide conversion tables or other mapping functions for analog input and analog output points that define how the input or output hardware values relate to the engineering units used.

.3	This function must accommodate non-linear relationships.

.4	If a conversion table type function is used, it must have a minimum of 10 individually definable segments.

.5	Provide capability to assign any user defined unit to the analog point (i.e. percent, Deg C, Deg F, etc.).

### .2	Digital Points

.1	Provide the capability to define in database whether a digital input point is normally open or normally closed.

.2	Provide the capability to assign any pair of engineering units to the relay open and relay closed positions of digital output points,  (i.e. start/stop, on/off, open/closed).

## 2.8	Software Controllers

.1	Provide controllers in each SAP and TUC.

.2	Provide, in each controller, the following set up and tuning capabilities:

.1	Direct or reverse acting.

.2	Output value to control, 0 to 100%.

.3	Set point.

.4	Proportional Gain.

.5	Integral gain.

.6	Derivative gain.

.7	Control loop bias.

.3	Provision shall exist for the modification of the above by OCL programs and/or the operator while on-line through a terminal.

## 2.9	Operator Control Language (OCL) Capabilities

.1	The stand alone panels (SAPs) and soft terminal unit controllers (TUCs) shall have the capability for the operator to develop and run custom application programs.  For this, the system shall have a proven OCL which shall be capable of reading the value and/or status of all system points and initiating both digital and analog control actions from any user defined combination of calculations and logical expressions which shall at a minimum include:

-	Addition, subtraction, multiplication and division;

-	Square roots, summations, absolute differences;

-	Logical ÒnotÓ, ÒandÓ, ÒorÓ, ÒnorÓ, ÒandÓ, Òless thanÓ, Ògreater thanÓ, and Òequal toÓ or their logical equivalents;

-	Time delays in seconds, minutes or hours;

-	Ability to embed comments in system generated documentation;

-	Ability to use time-of-day and day-of-year in algebraic calculations; and

-	Ability to use weekly and annual schedules.

.2	The supplied systemÕs OCL shall support the concept of output oriented code, or in other words, a program shall be generated for each controlling output or logical group of outputs.  Required programs for each system are listed in the generic start up logic, although manipulation will be required to achieve the intent in each vendorÕs system.

## 2.10	OCL Editor

.1	Provide a full screen editor to enable editing of the OCL programs source code down to character by character changes.

.2	Provide the capability in the editor of accepting programs from ASCII files that have been created on other MS-DOS compatible computers and word processors.

.3	If a point is removed from the database, show an error signal for undefined character on the appropriate line whenever a program using that point is viewed, edited or printed.

# PS 3 - HARDWARE FEATURES

## 3.1	Panel Definitions

.1	Stand-alone panels ( SAP’s ) shall be considered to be any panel connected to a primary communication network.  In addition, SAP’s shall control central plant equipment ( i.e. air handling unit equipment, boiler plant equipment, chiller plant equipment ).

.2	Terminal unit controllers ( TUC’s ) shall be considered to be any panel connected to a SAP through a  sub-communication network.  In addition, TUC’s shall control HVAC terminal devices serving one single thermostatic zone ( i.e. VAV terminal unit, dual-duct terminal unit, fan-coil terminal unit, water-loop heat pump unit ).

## 3.2	Power Conditioning

.1	Provide filters to protect the system from power line surges and voltage transients.

## 3.3	Power Failure Protection

.1	Provide automatic retention of RAM and real time clock from any power failure of at least SEVENTY-TWO (72) hours duration.  This feature will be checked during the commissioning phase.

.2	Provide for automatic restart of the system upon power return.

## 3.4	Hardware Failure Isolation

.1	Any component malfunction shall not damage any of the remaining components.

.2	Provide over voltage protection on inputs and outputs.

## 3.5	Ease of Hardware Replacement

.1	SAP and TUC replacement shall be possible without any hardware modification.

## 3.6	Database Back-Up and Off-Line Storage

.1	The system shall have the capability to be taken off line in the event of failure or for maintenance and returned to operation without the need for entering any portion of the software program manually.  To accomplish this, an off-line disk storage device shall be utilized to provide software backup and reload.

.2	On-site backup and verification of the entire system, with full applications software, shall be less than TWO (2) seconds per real point.  This feature will be checked during the commissioning phase.

## 3.7	Memory

.1	Each SAP on the main network proposed shall have enough random access memory (RAM) for all of the following:

.1	Trend Logs - One and a Half (1.5) TL for each input and output point connected to the SAP with 100 samples each.

.2	Totalizers - ONE (1) for each digital point connected to the SAP.

.3	Time Schedules - ONE (1) for every 3 output points connected to the SAP.

.4	Annual Schedules  - ONE (1) for every 6 output points connected to the SAP

.5	Controllers - TWO (2) for each analog output point connected to the SAP .

.6	Software Points - THREE (3) for each output point connected to the SAP .

.7	Operator Control Language (OCL) - TWENTY (20) syntactically correct lines each with at least 4 operators, for each output point connected to the SAP .

.8	Descriptor - ONE (1) for each user definable point, real or software, in the SAP.  In addition, on multi-SAP systems, every descriptor in the system must be accessible from every operator interface device.

.9	In the event there are TUCs networked to the SAP, which do not have their own memory meeting items .1 through .7, the SAP must have full memory for all TUC points as well as points connected directly.

.10	Provide with shop drawing submittal, calculations which confirm the foregoing RAM requirements are met for each SAP.

## 3.8	SAP Processing Speed

.1	Effective SAP Processing Speed - Maximum permissible execution time is TWO (2) seconds.  Execution time is defined as the time it takes the SAP CPU to execute all application software in the SAP, with no system timing errors, from some point in the software back to the same point, assuming full memory usage, as defined in Clause 3.7 above, while simultaneously responding to operator or terminal display requests and carrying out normal inter-SAP communications averaged over a ONE (1)-minute period.  This will be done during the commissionary phase by setting up a counter in each SAP and monitoring their counting rate.

## 3.9	System Display Speed

.1	The minimum time to change from one dynamic screen to another is 7 seconds.  This test will be carried out from a remote site with the Corporation’s standard modem and will be the average of 10 typical displays for the project.  Test will be carried out with the specified system configuration, excluding multi-user and alarming functions.

# PS 4 - INTRA-SYSTEM COMMUNICATION

## 4.1	Network Communications

### .1	Stand-Alone Panels (SAPs)

.1	Provide a fully networked system of SAPs which use a peer-to-peer communications protocol to support the distributed control features as specified herein.  Each SAP shall be connected directly to the network.  Each SAP shall have equal network access priority and shall not require a separate interface panel (gateway) to accomplish network communications.

.2	Provide a means to ensure communication integrity.

.3	To prevent damage to the system each data highway line shall be provided with a means of isolation, either optically or by some other means.

.4	Upon failure of the network to communicate information from one SAP to other SAPs, retain the last legitimate value of each point in the SAPs that require it, and continue to control the systems based on those values.  Failure of any SAP, or any part of a SAP on the network, shall not affect the ability of the network to communicate among the remaining SAPs.

.5	Each physical or virtual point shall have a user-definable, unique, system-wide logical point mnemonic.  The format of this point mnemonic shall conform to BCBC Point Naming Convention.  All point functions such as commands, overrides, trends, reports, logs and graphics shall only need to use this unique logical point mnemonic.

.6	Values, statusÕs and attributes of physical and software points from one SAP shall be available for use in any other SAPs.  Any broadcast points, send-receive blocks or any other form of table or database that is required to initialize and accomplish this function shall be created solely, and automatically, by the operating system, without the need for operator intervention.  Listings of physical and software points shall not include tables referred to in this paragraph.

### .2	Terminal Unit Controllers (TUCs)

For systems which include terminal unit controllers (TUCÕs).

.1	The terminal unit controllers (TUCs) shall incorporate all of the requirements for the stand-alone panels (SAPs), except for peer to peer communications (PS 4.1.1.1) and auto-networking provisions (PS 4.1.1.6).

.2	The auto-networking requirements defined in PS 4.1.1.6 for SAPs apply between the TUC and the SAP it is connected to. If the TUC is connected to the main peer to peer communication network, the full requirements of  PS 4.1.1.6 apply.

## 4.2	System  Processing Speed

.1	For multi SAP systems, the system processing speed is intended to address inter-SAP communications and will be checked during the commissioning phase by evaluating value updates from one SAP as received and displayed in another SAP.  This will be done by setting up a display of all SAP counters and checking how frequently each counter is updated on the refreshed display on site.

.2	Every counter shall show an updated value on the display within TWENTY (20) seconds of the previous update value appearing.  This feature will be checked during the commissioning phase.

# PS 5 - FIELD DEVICES

## 5.1	General

.1	This Clause contains a comprehensive range of field devices listed alphabetically by ÒPoint typeÓ code, not all of which will necessarily be applicable to this project.  Refer to the ÒPoint TypeÓ column on the points lists in Section 15930 to identify the devices relevant to this project.

.2	Some point types have a number as the last character in order to identify variations in a group of similar field devices.  For each separate point type or group of similar devices (common point type except for number) all items provided shall be the product of one manufacturer.

.3	All field devices shall be selected to have full compatibility with the SAPs, TUCs or other controls components being proposed.

.4	Any field device proposed for use which is not one of the products listed under ÒStandard of AcceptanceÓ will be evaluated by the CorporationÕs representative against the specified technical performance and the quality and characteristics of the products which are listed.  If any proposed field device is deemed not equivalent to the specification, then the controls contractor shall provide another device which does meet specification at no extra cost.

.5	The shop drawing submittal shall include technical data for all field devices listed in the points lists, specifically cross-referenced to the particular point type to facilitate the shop drawing review.

.6	Some devices may require different ranges, capacities, etc. in particular applications, even though the device or component is otherwise the same.  Where definition of such variations is required in the specifications or points lists, the point type will use suffixes, for example ÒDPS/xÓ or ÒDA1/xÓ.  The suffixes are explained in the ÒTechnical PerformanceÓ portion of each point type specification.

.7	The end-to-end accuracy required for analog devices shall include the combined effect of sensitivity, hysteresis, linearity and repeatability between the measured variable and the output at the operator interface device, or between the panel signal to the digital-to-analog converter and the controlled variable.

.8	Devices shall meet the specific requirements listed, and shall be compatible with respect to power supply, signal characteristics, or other factors with the CCS being proposed.  Power supplies shall be provided as required for any and all devices.

## 5.2	Point Type ÒCRSÓ

.1	Description - Control Relay Status ÒCRSÓ is used where the field device will be either:

-	an auxiliary dry contact, supplied as part of the equipment whose status will be monitored by this point, or

-	if there is no auxiliary dry contact on the equipment, a relay as specified in 2. and 3., provided by the control contractor.

.2	Technical Performance - a high impedance relay to produce a dry contact.

.3	Standard of Acceptance - Omron Model GSD, Veris Model 607 voltage bug

## 5.3	Point Type ÒCR1Ó

.1	Description - Control Relay (Solid State)

.2	Technical Performance - 240 V, 10 amp capacity.  SPST function.  Normally open (or normally closed) as required by points list or application complete with optical isolation.  Suitable for switching inductive AC loads.

.3	Standard of Acceptance		-  Electromatic - RS104240.

-  Potter & Brumfield EOTZ Series.

-  Grayhill 7052-04-C-12-S.

## 5.4	Point Type ÒCR2Ó

.1	Description - Control relay (dry contact electro-mechanical relay).

.2	Technical Performance - 240 V, 10 A to suit application.

.3	Standard of Acceptance		-  IDEC-RH Series.

-  Johnson R1020 series.

## 5.5	Point Type ÒCR3Ó

.1	Description - Control relay (Solid state relay suitable for switching D.C. loads).

.2	Technical Performance - 60 VDC.

.3	Standard of Acceptance 		-  Grayhill.

## 5.6	Point Type ÒCS1Ó

.1	Description - Current sensor (analogue).

.2	Technical Performance - Self powered, with insertion impedance loss less than 0.0006 ohms under all conditions.  End-to-end accuracy ± 2% of full scale at each range.  Ranges: 1.0 to 10.0 amps, low; 5 to 50 amps, middle; 20 to 200 amps, high; selectable by switch or by setting jumpers.

.3	Standard of Acceptance 		-  Greystone CS-150.

## 5.7	Point Type ÒCS2Ó

.1	Description - Current Sensor (switch).

.2	Technical Performance - Solid State N.O. AC switch.  Same ranges as point type ÒCS1Ó.  Manual adjustment of switch threshold setting.

.3	Standard of Acceptance 		-  Greystone CS-125.

## 5.8	Point Type ÒCV1Ó

.1	Description - Control Valve (2 way, 2 position)

.2	Technical Performance - Brass or bronze globe valve construction, with screwed ends.  Materials suitable for chilled water or hot water up to 125¼C.  24 VAC.  Working pressure, 875 kPa.  N.O. spring return.  Minimum close off pressure rating shall meet requirements in the points lists; if no requirement, minimum close off pressure rating shall be 70 kPa.

.3	Standard of Acceptance		-  Honeywell V8043 series

-  Johnson J-series

.4	Submittal Data - Submittal data shall include the proposed Cv rating for each control valve.  If a specific Cv is specified in the points list or on a valve schedule, ensure the control valve proposed has a similar Cv to that specified.

## 5.9	Point Type ÒCV2Ó

.1	Description - Control Valve (2 way, floating control).

.2	Technical Performance - Brass or bronze body, globe valve with equal percentage flow characteristic, screwed ends.  Materials suitable for chilled water or hot water up to 125¼C.  Working pressure 875 kPa.  24 VAC reversing motor drive.  Minimum close off pressure rating shall be 30 psi, or as stated in the points list, which ever is higher.

.3	Standard of Acceptance		-  Johnson

-  Honeywell

.4	Submittal Data - Submittal data shall include the proposed Cv rating for each control valve.  If a specific Cv is specified in the points list or on a valve schedule, ensure the control valve proposed has a similar Cv to that specified.

## 5.10	Point Type ÒCV3Ó

.1	Description - Control Valve (2 way modulating, non-spring-return).

.2	Technical Performance - Globe valve body, with equal percentage flow characteristics.  Materials suitable for chilled water or hot water up to 125¼C.  Modulating actuator with 0-10 VDC signal range, power to open and power to close.  Working pressure 875 kPa.

.3	Standard of Acceptance		-  Johnson

-  Honeywell

.4	Submittal Data - Submittal data shall include the proposed Cv rating for each control valve.  If a specific Cv is specified in the points list or on a valve schedule, ensure the control valve proposed has a similar Cv to that specified.

## 5.11	Point Type ÒCV4Ó

.1	Description - Control Valve (2 way, modulating, spring return).

.2	Technical Performance - Technical performance shall be as specified in 6.10.2.

.3	Standard of Acceptance		-  Johnson

-  Honeywell

.4	Submittal Data - Submittal data shall include the proposed Cv rating for each control valve.  If a specific Cv is specified in the points list or on a valve schedule, ensure the control valve proposed has a similar Cv to that specified.

## 5.12	Point Type ÒDA1/xÓ

.1	Description - Direct Coupled Damper Actuator (Electric, modulating, non-spring-return).

.2	Technical Performance			-  Power Voltage 24 VAC or 120 VAC.

-  Control Voltage 0 - 10 VDC.

Suffixes	-	ÒDA1/AÓ	-  50 in-lb torque capacity.

-	ÒDA1/BÓ	-  90 in-lb torque capacity.

-	ÒDA1/CÓ	- 130 in-lb torque capacity.

.3	Standard of Acceptance		-  Belimo NM-24SR or NM-24SRS (ÒDA1/AÓ)

-  Belimo SMC-24SR (ÒDA1/BÓ)

-  Belimo SM-24SR or SM-24SRS (ÒDA1/CÓ)

-  Johnson Controls M140-GGA (ÒDA1/AÓ)

-  Johnson Controls M150-GGA (“DA1/BÓ or ÒDA1/CÓ)

## 5.13	Point Type ÒDA2/xÓ

.1	Description - Damper Actuator (Electric, modulating, spring return).

.2	Technical Performance		-  Power voltage 24 VAC or 120 VAC

-  Control Voltage 0 - 10 VDC

Suffixes	-	ÒDA2/AÓ	-  50 in-lb torque capacity.

-	ÒDA2/BÓ	-  90 in-lb torque capacity.

-	“DA2/C”	-  133 in-lb torque capacity.

.3	Standard of Acceptance		-  Belimo FM-24SR, NF-24 SR (ÒDA2/AÓ)

-  Belimo AF24-SR  (“DA2/C”)

-  Johnson Controls M130-GGA (ÒDA2/AÓ only)

## 5.14	Point Type ÒDA3/xÓ

.1	Description - Damper Actuator (Electric, 2-position, non-spring-return).

.2	Technical Performance - Power Voltage 24 VAC or 120 VAC

Suffixes	-	ÒDA3/AÓ	-  75 in-lb torque capacity.

-	ÒDA3/BÓ	-  90 in-lb torque capacity.

-	ÒDA3/CÓ	-  130 in-lb torque capacity.

.3	Standard of Acceptance		-  Belimo NM-24 (ÒDA3/AÓ)

-  Belimo SMC-24 (ÒDA3/BÓ)

-  Belimo SM-24 (ÒDA3/C4/Ó)

## 5.15	Point Type ÒDA4/xÓ

.1	Description - Damper Actuator (Electric, 2-position, spring return).

.2	Technical Performance - Power Voltage, 24 VAC or 120 VAC.

Suffixes	-	ÒDA4/AÓ 	-  130 in-lb torque capacity.

.3	Standard of Acceptance		-  Belimo SF-24, AF-24, NF-24,  SF-120, AF-120, NF-120.

## 5.16	Point Type ÒDDCÓ

.1	Description - Point type ÒDDCÓ is used to describe on analog output which is to be connected to a piece of equipment not supplied by the controls contractor for the purpose of controlling that equipmentÕs operation in some way.  Examples would be an output to a variable speed drive to control its speed, or an output to a modulating chiller (or boiler) to control its operating output.

.2	The controls contractor shall provide wiring, and interface devices.

## 5.17	Point Type ÒDHSÓ

.1	Description - Duct mounted relative humidity sensor.

.2	Technical Performance - Operating range, 10% RH to 90% RH, over a 0¼C to 60¼C temperature range.  End-to-end accuracy ± 3% of operating range, with maximum temperature dependence of 0.2% per ¼C change.  200 mm long probe, with enclosure, for mounting in duct.

.3	Standard of Acceptance		-  Greystone HS-250-C-02

-  Hy-cal CT-829-A

## 5.18	Point Type ÒDPS/xÓ

.1	Description - Differential Pressure Sensor

.2	Technical Performance - Solid-state design, operating on capacitance principle, with non-interactive fine resolution, zero, and span adjustments.  End-to-end accuracy ± 2% of full scale pressure range, including temperature compensation.  Shall have integral filters at each air connection port.

Suffixes	-	ÒDPS/AÓ	-  0 to 25 Pa pressure range.

-	ÒDPS/BÓ	-  0 to 50 Pa pressure range.

-	ÒDPS/CÓ	-  0 to 75 Pa pressure range.

-	ÒDPS/DÓ	-  0 to 125 Pa pressure range.

-	ÒDPS/EÓ	-  0 to 250 Pa pressure range.

-	ÒDPS/FÓ		-  0 to 500 Pa pressure range.

-	ÒDPS/GÓ	-  0 to 750 Pa pressure range.

-	ÒDPS/HÓ	-  0 to 1250 Pa pressure range.

.3	Standard of Acceptance	-	Modus T20-xxx, T30-xxx, or T40-xxx to suit pressure range and application.

-  Autotran 700.

## 5.19	Point Type ÒDTS1/xÓ

.1	Description - Duct temperature sensor, with an averaging element.

.2	Technical Performance - Constructed of FT6 plenum rated cable or soft copper tubing, incorporating numerous temperature sensors encapsulated at equal distances along the length of the element.  The assembly acts as a single sensor, reporting the average temperature from all the individual sensors.  Operating range: 0¼C to 60¼C; end-to-end accuracy ±0.3¼C.  Assembly complete with wiring housing and mounting flange.

Suffixes	-	ÒDTS1/AÓ	-  3.5 m sensor cable length

ÒDTS1/BÓ	-  6.0 m cable length

.3	Standard of Acceptance		-  Greystone TE-200

-  Pre-con

## 5.20	Point Type ÒDTS2Ó

.1	Description - Duct temperature sensor, with probe type element.

.2	Technical Performance - Sensor encapsulated in a 200 mm long, 6 mm OD copper or stainless steel probe.  Operating range 0¼C to 60¼C; end-to-end accuracy ± 0.3¼C.  Assembly complete with wiring housing and mounting flange.

3.	Standard of Acceptance		-  Greystone TE-200-B-7-C

-  Pre-con

## 5.21	Point Type ÒEPT1Ó

.1	Description - Electro-pneumatic transducer.

.2	Technical Performance - The electro-pneumatic transducer receives a 0-10 VDC or 0-20 mA signal input, and produces a 3-15 psig pneumatic output signal to position damper and valve actuators.  The device shall come complete with a pneumatic output pressure gauge.

.3	Standard of Acceptance		-  Greystone EPT8500

-  Delta EPT750

## 5.22	Point Type ÒFRZÓ

.1	Description - ÒFreezestatÓ auto-reset , complete with auxiliary dry contact in order to provide a separate digital input to the DDC system.

.2	Technical Performance - Range: -10¼C to 15¼C; probe length 6 m.  Control responds to the lowest temperature along any 0.3 m of the entire length of the element.

.3	Standard of Acceptance		-  Penn A170-GA-1

## 5.23	Point Type ÒGAS1Ó

.1	Description - CO2 concentration sensor.

.2	Technical Performance - 0 - 2500 ppm ± 2% Full Scale.

.3	Standard of Acceptance		-  Quatrosense Environmental Ltd. QEL QTS - 2000.

## 5.24	Point Type ÒGAS2Ó

.1	Description - Carbon monoxide concentration sensor.

.2	Technical Performance - 0 - 125 ppm CO output drift < 2% signal per month.

.3	Standard of Acceptance		-  Quatrosense Environmental Ltd.

## 5.25	Point Type ÒGAS3Ó

.1	Description - flammable gas concentration sensor.

.2	Technical Performance -

.3	Standard of Acceptance 		-

## 5.26	Point Type ÒGAS4Ó

.1	Description - Refrigerant vapour concentration sensor.

.2	Technical Performance  -

.3	Standard of Acceptance		-

## 5.27	Point Type ÒGAS5Ó

.1	Description - Total volatile organic compounds (TVOCÕs) concentration sensor, designed for mounting within an occupied space.  This type of device is sometimes referred to as an indoor air quality sensor.

.2	Technical Performance -

.3	Standard of Acceptance		-

## 5.28	Point Type ÒLS1Ó

.1	Description - Photocell light level sensor, with analogue output related to light intensity.

.2	Technical Performance - Dark 1 meg ohm, bright 1.5 K ohm.

.3	Standard of Acceptance		-  Greystone PSR-1.

## 5.29	Point Type ÒLS2Ó

.1	Description - Photocell, adjustable light level switch.

.2	Technical Performance -

.3	Standard of Acceptance		-

## 5.30	Point Type ÒOS1Ó

.1	Description - Passive infrared occupancy sensor.

.2	Technical Performance  -

.3	Standard of Acceptance		-

## 5.31	Point Type ÒOTSÓ

.1	Description - Outside air temperature sensor.

.2	Technical Performance - 10K ohm thermistor sensor encapsulated in a 6 mm OD probe, complete with weatherproof enclosure, sun shield and mounting bracket.  Operating range: -35¼C to +50¼C.  End-to-end accuracy: ± 0.3¼C over the entire operating range.

.3	Standard of Acceptance 		-  Greystone TE-200-F, c/w 100 K ohm  parallel resistor.

## 5.32	Point  Type “PS1”

.1	Description  -Pipe Pressure Transducer.

.2	Technical Performance - Brazed  assembly with 300 series stainless steel parts that are in contact with the media, snap tract and circuit board c/w external pressure sensor and mounted in a NEMA 4 enclosure.  Accuracy ±  3% span from best fit straight line.

Inputs - 7.5 - 32 VDC, outputs - 4 - 20 ma or 1-5 VDC

Range  -  Suffix  A  -  0 - 350  kPa  -  Suffix  B  -  0 - 700  kPa

.3	Standard of Acceptance  		-  Greystone  PGS - 100

## 5.33	Point Type ÒPTS1Ó

.1	Description  - Pipe Temperature Sensor, immersion type .

.2	Technical Performance - 10K ohm thermistor sensor encapsulated in a 6 mm OD, 50 mm long probe, with screw fitting for insertion into a standard thermowell.  Sensor assembly to be complete with enclosure and thermowell.  Operating range: -10¼C to 100¼C. End-to-end accuracy: ± 0.3¼C over the entire operating range.

.3	Standard of Acceptance  		-  Greystone TE-200-C

## 5.34	Point Type ÒPTS2Ó

.1	Description - Pipe Temperature Sensor, strap-on type.

.2	Technical Performance - 10K ohm thermistor encapulated in a stainless steel pad designed for strap-on installation.  Assembly to be complete with solid-state circuitry in an enclosure and connecting cable to the thermistor.  Operating range: -10¼C to 100¼C.  End-to-end accuracy: ± 0.3¼C over the entire operating range.

.3	Standard of Acceptance		-  Greystone TE-200-E-7

## 5.35	Point Type ÒRHSÓ

.1	Description - Relative Humidity Sensor Room Type.

.2	Technical Performance - operating range:  10% RH to 90% RH, over a 0¼C to 60¼C temperature range.  End-to-end accuracy:  ± 3.0% of operating range, with maximum temperature dependence of 0.2% RH per ¼C change.  Assembly shall be complete with a baseplate for wall mounting, a rigid circuit board for all circuitry and the sensing element, and a ventilated enclosure.

.3	Standard of Acceptance		-  Greystone HS-150-B-02

-  Hy-cal C102-H

## 5.36	Point Type ÒRTS1Ó

.1	Description - Room temperature sensor complete with momentary override switch.

.2	Technical Performance - Assembly shall consist of a 10K ohm thermistor and related circuitry mounted on a circuit board/baseplate for wall mounting, complete with a vented, plastic enclosure.  Operating range: 10¼C to 30¼C.  End-to-end accuracy: ± 0.3¼C over the entire operating range.

.3	Standard of Acceptance			-  Greystone TE-200-AE-OR

## 5.37	Point Type ÒRTS2Ó

.1	Description - Room Temperature Sensor, security type.

.2	Technical Performance - Assembly shall consist of a 10K ohm thermistor and related circuitry mounted on a rigid, metal cover plate designed for mounting into a recessed junction box.  The sensing element shall be attached directly to the cover plate.  Operating range: 10¼C to 30¼C.  End-to-end accuracy:  ± 0.3¼C over the entire pressure range.

.3	Standard of Acceptance			-  Greystone TE-200-AS

## 5.38	Point Type ÒRTS3Ó

.1	Description - Room temperature sensor complete with momentary override switch, setpoint adjustment, and setpoint indication.

.2	Technical Performance - Assembly shall consist of a 10K ohm thermistor and related circuitry mounted on a rigid, metal cover plate designed for mounting into a recessed junction box.  The sensing element shall be attached directly to the cover plate.  Operating range: 10¼C to 30¼C.  End-to-end accuracy:  ± 0.3¼C over the entire pressure range.

.3	Standard of Acceptance			-  Greystone TE-200-IT

-  Delta Intellistat RTS406

## 5.39	Point Type ÒVS1Ó

.1	Description - Velocity sensor (single point flow sensor).

.2	Technical Performance - 0 - 3000 FPM Adjustable 4Ó - 16Ó ducts.  (Thermal anemometer technology).

.3	Standard of Acceptance			-  BELIMO.

## 5.40	Point Type ÒVS2Ó

.1	Description - Air velocity sensor with thermal anemometer technology, using differential pressure signal from a flow grid in duct or VAV box inlet.

.2	Technical Performance -

.3	Standard of Acceptance			-

## 5.41	Point Type ÒWPSÓ

.1	Description -  (Window Position Switch) Point type ÒWPSÓ is used to describe a digital input connected to a dry contact which is part of a magnetic proximity switch on openable sections of glazing.  The dry contact will be open when the window is open, and closed when the window is closed.

.2	If the window supplier provides the proximity switches, and wiring from their dry contacts, to 300 mm above the window head above the openable section, use the CRS designation for the point.

# PS 6 - OPERATING SYSTEM SOFTWARE POINT REQUIREMENTS

## 6.1	General

This clause contains a list of system points, not all of which will be applicable to this project.  Refer to the "Point Type" column on the points lists in Section 15930 to identify the points relevant to this project.

The contractor shall create and name all points indicated in the points lists.  Software points shall have the same characteristics on the graphic screens as the real or hardware points.  Additional points may be required by some systems to comply with the intent of the Generic Start-up Logic.  All software points to be located on the graphic screens as shown in the Graphics Guidelines.

## 6.2	Point Type "AL"

Description: Alarm Point

Set up alarm points, if required, so that nuisance alarms are minimized.  Name as per points lists.  First name in "notes" is alarmed point while second is associated system point.  Route alarms to "AR" point and to the site terminal or modem.

## 6.3	Point Type "AS"

Description: Annual Schedule

Annual schedules will allow the operator to set up the statutory holidays one year in advance.  When assigned to a weekly schedule the annual schedule will allow the weekly schedule to be overridden.

## 6.4	Point Type "CO"

Description: Controller

A point which allows a software controller to be set up as P, PI, or PID.  The measured variable is noted as the first name in the "notes" column of the points lists, while the setpoint is the second.  Set up as required to provide stable operation with no "dithering" or hunting.  Output units are 0% to 100%.

## 6.5	Point Type "PG"

Description: Program

This is the nomenclature for the point which contains the OCL programs that allow writing of the Òif, then, elseÓ statements.  Set up as detailed in the Graphic Guidelines.

## 6.6	Point Type "TL"

Description: Trend Log

Trend log points to be set up as detailed in the points lists and PS 9.  Points list trend logs have the points noted in the "notes" column separated by commas, e.g. HCV,SAT_SP,SAT,HCP.  Name as per points lists or BCBC Point Naming Convention if not on points lists.

## 6.7	Point Type "TZ"

Description: Totalizers

Set up totalizers for each digital output point in the system, except for outputs to floating point devices.  Name as per points list with units as hours.

## 6.8	Point Type "V"

Description: Variable

Variable or software points may be analog or digital as required. Set up as required in the points lists with the proper units, and as required to comply with the intent of the generic start-up logic.

## 6.9	Point Type "WS"

Description: Weekly Schedule

Weekly schedules provide the software time clock for use in OCL.  Values are on or off.  Set up with times as directed by the Owner’s representative.