## 6_0
B.C.BUILDINGS CORP. - CCS POINT NAMING CONVENTION
(SZ) SINGLE ZONE AIR SYSTEM
|  | MNEMONIC |  | MNEMONIC DESCRIPTION | EXAMPLES
| SYS. | POINT | FUNC.
| SZ* |  |  | Single Zone System* | SZ, SZI
|  | SF |  | Supply Fan | SZ1_SF
|  | RF |  | Return Fan | SZ1_RF
|  | EF |  | Exhaust Fan | SZ1_EF
|  | SAT |  | Supply Air Temperature | SZ1_SAT
|  | RAT |  | Return Air Temperature | SZ1_RAT
|  | MAT |  | Mixed Air Temperature | SZ1_MAT
|  | SAH |  | Supply Air Humidity | SZ1_SAH
|  | RAH |  | Return Air Humidity | SZ1_RAH
|  | MAD |  | Mixed Air Dampers | SZ1_MAD
|  | OAD |  | Outside Air Dampers | SZ1_OAD
|  | EAD |  | Exhaust Air Dampers | SZ1_EAD
|  | CCV |  | Cooling Coil Valve | SZ1_CCV
|  | CLG |  | Cooling System | SZ1_CLG
|  | HCV |  | Heating Coil Valve | SZ1_HCV
|  | HTG |  | Heating System | SZ1_HTG
|  | PCV |  | Preheat Coil Valve | SZ1_PCV
|  | DX |  | Direct Expansion Valve | SZ3_DX2
|  | CCP |  | Cooling Coil Pump | SZ1_CCP
|  | HCP |  | Heating Coil Pump | SZ1_HCP
|  | PCP |  | Preheat Coil Pump | SZ1_PCP
|  | ECP |  | EvaporativeCooling Pump | SZ1_ECP
|  | FRZ |  | Freeze Detection | SZ1_FRZ
|  | RT |  | Room Temperature | SZ1_RT1
|  |  | S | Status | SZ1_PCP3_S
|  |  | SP | Setpoint | SZ1_SAT_SP
|  |  | CO | Controller | SZ1_SAT_CO
|  |  | HL | High Limit | SZ1_SAT_HL
|  |  | LL | Low Limit | SZ1_MAT_LL
|  |  | TZ | Totalizer | SZ1_SF_TZ
|  |  | TL | Trend Log | SZ1_TL
|  |  | MODE | Mode | SZ1_HTG_MODE
|  |  | PG | Program | SZ1_PG
|  |  | AL | Alarm | SZ1_SAT_AL
B.C.BUILDINGS CORP. - CCS POINT NAMING CONVENTION
(MZ) MULTI-ZONE AIR SYSTEM
|  | MNEMONIC |  | MNEMONIC DESCRIPTION | EXAMPLES
| SYS. | POINT | FUNC.
| MZ* |  |  | Multi-Zone System* | MZ,MZ1
|  | SF |  | Supply Fan | MZ1_SF
|  | RF |  | Return Fan | MZ1_RF
|  | EF |  | Exhaust Fan | MZ1_EF
|  | RAT |  | Return Air Temperature | MZ1_RAT
|  | MAT |  | Mixed Air Temperature | MZ1_MAT
|  | CDT |  | Cold Deck Temperature | MZ1_CDT
|  | HDT |  | Hot Deck Temperature | MZ1_HDT
|  | SAH |  | Supply Air Humidity | MZ1_SAH
|  | RAH |  | Return Air Humidity | MZ1_RAH
|  | MAD |  | Mixed Air Dampers | MZ1_MAD
|  | OAD |  | Outside Air Dampers | MZ1_OAD
|  | EAD |  | Exhaust Air Damper | MZ1_EAD
|  | CCV |  | Cooling Coil Valve | MZ1_CCV
|  | CLG |  | Cooling System | MZ1_CLG
|  | HCV |  | Heating Coil Valve | MZ1_HCV
|  | HTG |  | Heating System | MZ1_HTG
|  | PCV |  | Preheat Coil Valve | MZ1_PCV
|  | DX |  | Direct Expansion Valve | MZ1_DX2
|  | CCP |  | Cooling Coil Pump | MZ1_CCP
|  | HCP |  | Heating Coil Pump | MZ1_HCP
|  | PCP |  | Preheat Coil Pump | MZ1_PCP
|  | ECP |  | Evaporative Cooling Pump | MZ1_ECP
|  | FRZ |  | Freeze Detection | MZ1_FRZ
|  | Z*** |  | Zone *** Control | MZ1_Z8
|  | ¦----> | D | Deck Mixing Dampers | MZ1_Z8D
|  | ¦----> | RT | Room Temperature | MZ1_Z8_RT
|  | ¦----> | SAT | Supply Air Temp. | MZ1_Z4_SAT
|  |  | S | Status | MZ1_PCP4_S
|  |  | SP | Setpoint | MZ1_SAT_SP
|  |  | CO | Controller | MZ1_Z8_CO
|  |  | MIN | Minimum | MZ1_RT_MIN
|  |  | AVG | Average | MZ1_RT_AVG
|  |  | MAX | Maximum | MZ1_ZD_MAX
|  |  | TZ | Totalizer | MZ1_SF_TZ
|  |  | TL | Trend Log | MZ1_TL
|  |  | MODE | Mode | MZ1_CLG_MODE
|  |  | PG | Program | MZ1_MAD_PG
|  |  | AL | Alarm | MZ1_MAT_AL
B.C.BUILDINGS CORP. - CCS POINT NAMING CONVENTION
(DD) DUAL DUCT AIR SYSTEM
|  | MNEMONIC |  | MNEMONIC DESCRIPTION | EXAMPLES
| SYS. | POINT | FUNC.
| DD* |  |  | Dual Duct System* | DD,DD1
|  | SF |  | Supply Fan | DD1_SF
|  | RF |  | Return Fan | DD1_RF
|  | EF |  | Exhaust Fan | DD1_EF
|  | SAT |  | Supply Air Temperature | DD1_SAT
|  | RAT |  | Return Air Temperature | DD1_RAT
|  | MAT |  | Mixed Air Temperature | DD1_MAT
|  | CDT |  | Cold Deck Temperature | DD1_CDT
|  | HDT |  | Hot Deck Temperature | DD1_HDT
|  | SAH |  | Supply Air Humidity | DD1_SAH
|  | RAH |  | Return Air Humidity | DD1_RAH
|  | MAD |  | Mixed Air Dampers | DD1_MAD
|  | OAD |  | Outside Air Dampers | DD1_OAD
|  | EAD |  | Exhaust Air Dampers | DD1_EAD
|  | CCV |  | Cooling Coil Valve | DD1_CCV
|  | DX |  | D X Cooling Stage | DD1_DX1
|  | CLG |  | Cooling System | DD1_CLG
|  | HCV |  | Heating Coil Valve | DD1_HCV
|  | PCV |  | Preheat Coil Valve | DD1_PCV
|  | HTG |  | Heating System | DD1_HTG
|  | CCP |  | Cooling Coil Pump | DD1_CCP
|  | HCP |  | Heating Coil Pump | DD1_HCP
|  | PCP |  | Preheat Coil Pump | DD1_PCP
|  | FRZ |  | Freeze Detection | DD1_FRZ
|  |  | B | Box *** Terminal Equip | DD1_B216
|  | ¦----> | D | Box Dampers | DD1_B216D
|  | ¦----> | RT | Room Temperature | DD1_B216_RT
|  |  | S | Status | DD1_PCP_S
|  |  | SP | Setpoint | DD1_SAT_SP
|  |  | CO | Controller | DD1_B216_CO
|  |  | MIN | Minimum | DD1_RT_MIN
|  |  | AVG | Average | DD1_D_AVG
|  |  | MAX | Maximum | DD1_RT_MAX
|  |  | MODE | Mode | DD1_CLG_MODE
|  |  | TZ | Totalizer | DD1_SF_TZ
|  |  | TL | Trend Log | DD1_TL
|  |  | PG | Program | DD1_PG
|  |  | AL | Alarm | DD1_SF_AL
B.C.BUILDINGS CORP. - CCS POINT NAMING CONVENTION
(TR) TERMINAL REHEAT AIR SYSTEM
|  | MNEMONIC |  | MNEMONIC DESCRIPTION | EXAMPLES
| SYS. | POINT | FUNC.
| TR* |  |  | Term Reheat Sys* | TR,TR1
|  | SF |  | Supply Fan | TR1_SF
|  | RF |  | Return Fan | TR1_RF
|  | EF |  | Exhaust Fan | TR1_EF
|  | SAT |  | Supply Air Temperature | TR1_SAT
|  | RAT |  | Return Air Temperature | TR1_RAT
|  | MAT |  | Mixed Air Temperature | TR1_MAT
|  | SAH |  | Supply Air Humidity | TR1_SAH
|  | RAH |  | Return Air Humidity | TR1_RAH
|  | MAD |  | Mixed Air Dampers | TR1_MAD
|  | OAD |  | Outside Air Dampers | TR1_OAD
|  | EAD |  | Exhaust Air Dampers | TR1_EAD
|  | CCV |  | Cooling Coil Valve | TR1_CCV
|  | CLG |  | Cooling System | TR1_CLG
|  | HCV |  | Heating Coil Valve | TR1_HCV
|  | HTG |  | Heating System | TR1_HTG
|  | PCV |  | Preheat Coil Valve | TR1_PCV
|  | CCP |  | Cooling Coil Pump | TR1_CCP
|  | HCP |  | Heating Coil Pump | TR1_HCP
|  | PCP |  | Preheat Coil Pump | TR1_PCP
|  | DX |  | Direct Expansion Valve | TR1_DX2
|  | ECP |  | Evaporative Cooling Pump | TR1_ECP
|  | FRZ |  | Freeze Detection | TR1_FRZ
|  | RT |  | Room Temperature | TR1_RT5
|  | Z*** |  | Zone *** Terminal Equip | TR1_Z8
|  | ¦----> |  | Reheat Coil Valve | TR1_Z8_RCV
|  | ¦----> |  | Room Temperature | TR1_Z8_RT
|  | ¦----> |  | Perim Rad Valve | TR1_Z8_RAD
|  | ¦----> |  | Perim Panel Valve | TR1_Z8_PAN
|  |  | S | Status | TR1_PCP_S
|  |  | SP | Setpoint | TR1_SAT_SP
|  |  | CO | Controller | TR1_Z8_CO
|  |  | LL | Low Limit | TR1_MAT_LL
|  |  | TZ | Totalizer | TR1_SF_TZ
|  |  | TL | Trend Log | TR1_TL
|  |  | MODE | Mode | TR1_CLG_MODE
|  |  | PG | Program | TR1_MAD_PG
|  |  | AL | Alarm | TR1_DX2_AL
B.C.BUILDINGS CORP. - CCS POINT NAMING CONVENTION
(VV) VARIABLE VOLUME AIR SYSTEM
|  | MNEMONIC |  | MNEMONIC DESCRIPTION | EXAMPLES
| SYS. | POINT | FUNC.
| VAV |  |  | VAV System* | VAV,VAV1
| V** |  |  | VAV System For # > 9 | V12
|  | EF |  | Exhaust Fan | VAV1_EF
|  | SF |  | Supply Fan | VAV1_SF
|  | SFV |  | Supply Fan Vanes | VAV1_SFV
|  | SF_ASD |  | Supply Fan Variable Speed | VAV1_SF_ASD
|  | RF |  | Return Fan | VAV1_RF
|  | RFV |  | Return Fan Vanes | VAV1_RFV
|  | RF-ASD |  | Return Fan Variable Speed | VAV1_RF_ASD
|  | SVP |  | Supply Velocity Press | VAV1_SVP
|  | RVP |  | Return Velocity Press | VAV1_RVP
|  | DSP |  | Duct Static Pressure | VAV1_DSP
|  | BSP |  | Building Static Pressure | VAV1_BSP
|  | SAT |  | Supply Air Temperature | VAV1_SAT
|  | RAT |  | Return Air Temperature | VAV1_RAT
|  | MAT |  | Mixed Air Temperature | VAV1_MAT
|  | SAH |  | Supply Air Humidity | VAV1_SAH
|  | RAH |  | Return Air Humidity | VAV1_RAH
|  | MAD |  | Mixed Air Dampers | VAV1_MAD
|  | OAD |  | Outside Air Dampers | VAV1_OAD
|  | EAD |  | Exhaust Air Dampers | VAV1_EAD
|  | CCV |  | Cooling Coil Valve | VAV1_CCV
|  | CLG |  | Cooling System | VAV1_CLG
|  | HCV |  | Heating Coil Valve | VAV1_HCV
|  | HTG |  | Heating System | VAV1_HTG
|  | PCV |  | Preheat Coil Valve | VAV1_PCV
|  | DX |  | Direct Expansion Valve | VAV1_DX3
|  | CCP |  | Cooling Coil Pump | VAV1_CCP
|  | HCP |  | Heating Coil Pump | VAV1_HCP
|  | PCP |  | Preheat Coil Pump | VAV1_PCP
|  | ECP |  | Evaporative Cooling Pump | VAV1_ECP
|  | FRZ |  | Freeze Detection | VAV1_FRZ
|  | B*** |  | Box *** Term Equip Ctrl | VAV1_B216
|  | ¦----> | D | VAV Box Dampers | VAV1_B216D
|  | ¦----> | F | VAV Box Flow Rate | VAV1_B101F
|  | ¦----> | RT | VAV Room Temperature | VAV1_B216_RT
|  | ¦----> | V | VAV Heating Valve | V12_B216V
|  | ¦----> | RAD | VAV Rad Control | V12_B216_RAD
|  |  | S | Status | V12_PCP_S
|  |  | SP | Setpoint | V12_SAT_SP
|  |  | CO | Controller | V12_HCV_CO
|  |  | TZ | Totalizer | V12_SF_TZ
|  |  | TL | Trend Log | V12_TL
|  |  | MODE | Mode | V12_HTG_MODE
|  |  | PG | Program | V12_PG
|  |  | AL | Alarm | V12_FRZ_AL
B.C.BUILDINGS CORP. - CCS POINT NAMING CONVENTION
(BLR) BOILER SYSTEM
|  | MNEMONIC |  | MNEMONIC DESCRIPTION | EXAMPLES
| SYS. | POINT | FUNC.
| BLR |  |  | Boiler System | BLR, BLR1
| HTG |  |  | Heating System | HTG_P
|  | ENBL |  | Enable | BLR_ENBL
|  | SWT |  | Supply Water Temp | BLR_SWT
|  | RWT |  | Return Water Temp | BLR_RWT
|  | GV |  | Gas Valve | BLR-GV
|  | LO |  | Low Fire gas or oil | BLR_LO
|  | HI |  | High Fire gas or oil | BLR_HI
|  | EL |  | Electric Boiler Stage | BLR_EL1
|  | P |  | Pump | BLR_P4
|  | FS |  | Flow Switch | BLR_FS
|  |  | S | Status | BLR_P4_S
|  |  | SP | Setpoint | BLR_SWT_SP
|  |  | CO | Controller | BLR_GV_CO
|  |  | TZ | Totalizer | BLR_TZ
|  |  | TL | Trend Log | BLR_TL
|  |  | PG | Program | BLR_PG
|  |  | MODE | Mode | HTG_MODE
|  |  | AL | Alarm | BLR_AL
B.C.BUILDINGS CORP. - CCS POINT NAMING CONVENTION
HEATING WATER SYSTEMS
|  | MNEMONIC |  | MNEMONIC DESCRIPTION | EXAMPLES
| SYS. | POINT | FUNC.
POINT
| HTG |  |  | Heating | HTG
| RAD |  |  | Radiation System | RAD
| RHT |  |  | Reheat System | RHT
| PHT |  |  | Preheat System | PHT
| PAN |  |  | Radiant Panel System | PAN
| GLY |  |  | Glychol System | GLY
| DHW |  |  | Domestic Hot Water System | DHW
|  | SWT |  | Supply Water Temp | RAD_SWT
|  | RWT |  | Return Water Temp | HTG_RWT
|  | SWT |  | Supply Glycol Temp | GLY_SWT
|  | RGT |  | Return Glycol Temp | GLY_RWT
|  | V |  | Control Valve | PAN_V
|  | P |  | Pump | DHW_P5
|  | FS |  | Flow Swich | HTG_FS
|  |  | S | Status | RAD_P4_S
|  |  | SP | Setpoint | RHT_SWT_SP
|  |  | CO | Controller | RAD_SWT_CO
|  |  | TZ | Totalizer | PHT_P2_TZ
|  |  | TL | Trend Log | RAD_TL
|  |  | MODE | Mode | HTG_MODE
|  |  | PG | Program | DHW_PG
|  |  | AL | Alarm | RAD_P4_AL
B.C.BUILDINGS CORP. - CCS POINT NAMING CONVENTION
CHILLED WATER SYSTEM
|  | MNEMONIC |  | MNEMONIC DESCRIPTION | EXAMPLES
| SYS. | POINT | FUNC.
| CLR |  |  | Chiller System | CLR,CLR1
| CT |  |  | Cooling Tower | CT
| CLG |  |  | Cooling System | CLG
|  | ENBL |  | Enable | CLR_ENBL
|  | SWT |  | Supply Water Temp | CT_SWT
|  | RWT |  | Return Water Temp | CT_RWT
|  | BPV |  | Bypass Valve | CT_BPV
|  | V |  | Valve | CLG_V
|  | CR |  | Chiller Reset | CLR_CR
|  | CL |  | Chiller Limit | CLR_CL
|  | CS |  | Compressor Stage | CLR_CS1
|  | VANE |  | Chiller Vanes | CLR_VANE
|  | P |  | Pump | CLG_P3
|  | D |  | Damper | CT_D
|  | P_ASD |  | Variable Speed Pump | CLG_P_ASD
|  | F |  | Fan | CT_FAN1
|  | DV |  | Dump Valve | CT_DV
|  | FS |  | Flow Swich | CLR_FS
|  |  | S | Status | CLG_P4_S
|  |  | SP | Setpoint | CLR_VANE_SP
|  |  | CO | Controller | CLG_V_CO
|  |  | TZ | Totalizer | CLR_CS1_TZ
|  |  | TL | Trend Log | CT_TL
|  |  | PG | Program | CT_PG
|  |  | MODE | Mode | CLG_MODE
|  |  | AL | Alarm | CLR_CS1_AL
B.C.BUILDINGS CORP. - CCS POINT NAMING CONVENTION
WATER LOOP
(HP) HEAT PUMP SYSTEM
|  | MNEMONIC |  | MNEMONIC DESCRIPTION | EXAMPLES
| SYS. | POINT | FUNC.
| HP* |  |  | Heat Pump System* | HP
|  | CTF |  | Cooling Tower Fan | HP_CTF
|  | CTP |  | Cooling Tower Pump | HP_CTP
|  | P |  | Pump | HP_P1
|  | SWT |  | Loop Supply Temperature | HP_SWT
|  | RWT |  | Loop Return Temperature | HP_RWT
|  | CV |  | Cooling Valve | HP_CV
|  | HV |  | Heating Valve | HP_HV
|  | BLR |  | Boiler | HP_BLR
|  |  |  | Ht.Pump *** Terminal Equip | HP216
|  | ¦----> | C | Compressor | HP216_C
|  | ¦----> | F | Fan Control | HP216_F
|  | ¦----> | RT | Room Temperature | HP216_R
|  | ¦----> | REV | Mode (HTG/CLG) | HP216_REV
|  | ¦----> | SAT | Supply Air Temp | HP216_SAT
|  |  | S | Status | HP_P1_S
|  |  | SP | Setpoint | HP_SWT_SP
|  |  | CO | Controller | HP_RWT_CO
|  |  | MIN | Minimum | HP_RT_MIN
|  |  | AVG | Average | HP_RT_AVG
|  |  | MAX | Maximum | HP_RT_MAX
|  |  | TZ | Totalizer | HP_P1_TZ
|  |  | TL | Trend Log | HP_TL
|  |  | PG | Program | HP_PG
|  |  | AL | Alarm | HP_RT_MIN_AL
NOTE: Position of reversing valve will be as per units.
ie, Point Name = hp216_rev ,Units = heat or cool
B.C.BUILDINGS CORP. - CCS POINT NAMING CONVENTION
(TP) TEMPERATURE PREDICTOR
|  | MNEMONIC |  | MNEMONIC DESCRIPTION | EXAMPLES
| SYS. | POINT | FUNC.
| TP |  |  | Temperature Predictor | TP
|  | OAS |  | Outside Air Sensor | TP_OAS
|  | OAT |  | Outside Air Temp | TP_OAT
|  | PHT |  | Predicted High Temp | TP_PHT
|  | PLT |  | Predicted Low Temp | TP_PLT
|  | DH |  | Day's High Temperature | TP_DH
|  | DL |  | Day's Low Temperature | TP_DL
|  | YTD |  | Yesterday's Temp Diff | TP_YTD
|  | BOT |  | Building Objective Temp. | TP_BOT
|  | HDH |  | Hour of Day's High | TP_HDH
|  | HDL |  | Hour of Day's Low | TP_HDL
|  | SUN |  | Hour of Sunrise | TP_SUN
|  |  | PG | Program | TP_PG